Hamilton Health Sciences

Infrastructure Specifications

For Data/Voice and other Low Voltage Communications

November 2006 V1.0

Revised May 2007 V 1.1

Revised July 2007 V1.2

Revised October 2007 V1.3

Revised February 2008 V1.4

Revised April 2008 V1.5

Revised August 2009 V1.6

Revised March 2010 V1.7

Revised February 2012 V1.8

Revised September 2012 V1.9

Revised March 2013 V1.10

Revised June 2013 V1.11

Revised April 2016 V1.12

Created by:  Aurelio (Al) Caruso

Updated by:  same as above – May 2016

Preface

This infrastructure specification is a Hamilton Health Sciences document as it relates to the following:

Communication room build, Rack system build, new building design

CAT 6 UTP, CAT6A UTP, Fiber Optic and Voice trunk cabling, other cabling

Wireless Access Points

Installer/Installation

UPS/Power

HHS Cabling Direction

Existing Cabling Decommissioning (Renovation)

Existing Communication Room Relocation

The information in this specification is standards to be adhered to at Hamilton Health Sciences for on-site and remote services.

This document serves the following departments:

HITS (Health Information Technology Services)

Telecom

Security (where applicable)

Biomedical Engineering (where applicable)

Multi-Media (where applicable)

Facilities Management (not limited to: Nurse Call, Fire alarm, etc - where applicable)

This document is to be used by:

Capital Development

Third party Engineering Consultant

Third party Contractors

HHS Facilities Management Department

This document is to be used for:

New building/communication room builds

New communication room builds within existing buildings

Existing communication room builds (in whole or part – where possible)

All areas within new and existing buildings

HHS external points of presence.

This general document is not to be considered signoff from the above mentioned departments for projects.  For every project, there will need to be departmental engagement for signoff of infrastructure required.  The application of the standards in this document may differ slightly with each project, in particular with existing communication room builds.  This specification is a living document subject to change as required.

Note:  This document is write-protected for the safety of Hamilton Health Sciences.

Table of Contents:

Item							Page

- Communication Standards				4

- Communication Room Build				5

- Communication Room Layout			6

- Relay Rack Build					7

- Relay Rack Layout					8

- Cabling – Fiber Optic Specifications			9, 10

- Cabling – Copper Specifications			11, 12, 13, 14

- UPS Specifications for Communication Room	15

- Wireless Access Point Survey/Installation		16, 17, 18

- Labeling						19, 20, 21

- Installer Approval/Certification			22

- Installation Warranty					22

- Documentation					23

- Execution – Coordination				23

- Testing and Verification				24, 25

- Voice Trunk Cabling					26, 27

- Wired/Wireless Guidelines				28

- HHS Cabling Direction				29, 30

- Power Requirements for devices			31

- Current communication room locations/ID’s		32, 33, 34, 35

- Existing Cabling Decommissioning (Renovation)	36

- Existing Communication Room Relocation               37, 38

- Cabling practices for MUMC - HHS vs University	39

- New building – construction requirements		40

- Communication Standards

  - TIA/EIA-568-B Commercial Building Telecommunications Wiring Standard

  - CAN/CSA T529 Design Guidelines for Telecommunications Wiring Systems in Commercial Buildings.

  - ANSI/TIA-568-C.0, Generic Telecommunications Cabling for Customer Premises, February 2009

  - ANSI/TIA-568-C.1, Commercial Building Telecommunications Cabling Standard, February 2009

  - ANSI/TIA-568-C.2, Balanced Twisted-Pair Telecommunications Cabling and Components Standards, August 2009

  - ANSI/TIA-568-C.3, Optical Fiber Cabling Components Standard, June 2008.

  - TIA/EIA-569-B, Commercial Building Standard for Telecommunications Pathways and Spaces, October, 2004.

  - ANSI/TIA-606, Administration Standard for Commercial Telecommunications Infrastructure, May, 2006.

  - IEEE Std 802.3(tm)-2008 Part 3: Carrier sense multiple access with collision detection (CSMA/CD) access method and physical layer specifications.

  - IEEE Std 802.3(tm)-2008 Part 3: Carrier sense multiple access with collision detection (CSMA/CD) access method and physical layer specifications.

  - IEEE 802.3bc-2009, Part 3: Carrier Sense Multiple Access with Collision Detection (CSMA/CD) Access Method and Physical Layer Specifications.  Amendment 2: Ethernet Organizationally Specific Type, Length, Value (TLVs).

- ANSI/TIA-1179 “Healthcare Facility Telecommunications Infrastructure”

- Communication Room Build

The communication room build will consist of the following:

- Minimal 15 feet by 20 feet inside footprint

- Over head lighting on both sides of the rack system and other side of fencing between HITS/Telecom area and 3rd party area, within room. On emergency power.

- Manual light switches by doors (not motion sensor)

- Six emergency power duplex receptacles (separate circuits) (six 20A) on backside of racks (as identified) to satisfy HITS, Telecom and any other hospital department

- Three normal power duplex receptacle (three 20A) on backside of racks (as identified) to satisfy HITS, Telecom and any other hospital department

- Telephone wall jacks by doors

- Telephones

- Climate controlled air handling (brought from outside of room to within room)

- Door locks – swipe system

- Top to bottom fire rated wall board all the way around inside of room

- Normal power duplex receptacles on wall for Housekeeping use

- Additional emergency duplex receptacles on back and side walls as required for wall mount systems in 3rd party area

- CAT 6A walljacks on back and side walls as required for wall mount systems

- Wall mounted wire manager rail for voice pig tail patch cables (from rack to backboard) (or overhead tray system)

- Grounding system for racks

- There is to be no overhead Air Conditioner or other equipment, ducts, water pipes, etc inside the room - only lighting and cable tray overhead

- No water pipes of any sort within the room.  No washrooms adjacent or above.

- Sealed floor for dust prevention

- Communication room to be situated off of main hallway, not off sub hallway within staff office/clinical areas.

- There is to be no wall board low voltage systems either on front side or back side of racks, on the walls.  As well, no wall board low voltage systems on side walls. See below for communication room layout.

There must be signoff by HITS for approval of multiple department occupation of data/voice communication room and location of their respective equipment in order to ensure co-occupancy will not be to the detriment of HITS and anyone else occupying the room.

Please see Item 3.  Communication Room Layout (next page) for all requirements stated above.

3.  Communication Room Layout

Revised

Note 1:  Grounding bar system to be placed down low on back wall behind racks.

Rationale for increase of room size from 11’ x 12’ to 15’ x 20’: Newest network equipment on racks is longer in depth. Increasing wall mount systems for Engineering and Security.  Space requirement (by governed code) between end of last rack and wall for access from front to back side.

- Relay Racks Build

The rack build system will consist of the following:

- Three 84” high racks

- 10” or 12” vertical wire managers between the racks and outside of racks

- 48 port CAT 6A patch panels

- 4U horizontal wire managers (1 per rack), installed at top

- Racks bolted to floor, top side of racks tied off to overhead or sidewall

- Laptop sliding shelf

Note:  HHS standardized on Cisco networking equipment in 1999.  PANDUIT is the Cisco certified cabling partner.

The rack build system will be PANDUIT specific:

- Panduit racks - Part # R2PS

- Panduit 10" Patch Runner Vertical Manager - Part # PRVF10

- Panduit 10" Patch Runner Vertical Manager Door - Part # PRD10

- Panduit 12" Patch Runner Vertical Manager - Part # PRVF12

- Panduit 12" Patch Runner Vertical Manager Door - Part # PRD12

- Panduit Angled Modular Patch Panel 48 port - Part # CPPLA48WBLY

- Panduit Horizontal Wire Manager – Part # NMF4

Patch panels:

- 48 port, 2U modular jack panels wired to 568A or 568B configuration (General/Henderson – A, MUMC/Chedoke – B, St. Peters – A)

- Panels shall be complete with Cat 6A PANDUIT modular jacks as required

- Quantities as required

For existing, older communication rooms with existing CableTalk rack system, the following is required:

- Panduit Flat Modular Patch Panel 48 port - Part # CP48BLY

- CableTalk 2U Horizontal Wire Manager

- CableTalk 84” rack (from storage stock)

- CableTalk 8” vertical wire manager (from storage stock)

- CableTalk overhead manager - CTH-CMT-21-B

To be determined at cabling requirements stage.

5. Relay Racks Layout

The relay rack layout will be as follows:

- Three racks with vertical management will be placed together in a line closest to the far wall away from the door – See Item 3. Communication Room Layout previous.

- The equipment and patch panels will be front facing to the fencing separation (with door) with the equipment extending out the back of relay back.  See Item 3. Communication Room Layout previous.

Vertical real estate on the racks will be setup as follows from top to bottom:

Top down for first rack:

- Horizontal wire manager at top of each rack (4U)

- Fibre optic patch panel

- HITS/Telecom equipment

- UPS/s

- 1U spacer between each of the above mentioned

Top down for second rack:

- Horizontal wire manager at top of each rack (4U)

- Copper patch panels

Top down for third rack:

- Horizontal wire manager at top of each rack (4U)

- Other department equipment

- UPS/s

Note:  No copper patch panels on the equipment rack.

BioMed and Hospitality Network, other - will provide their own UPS and switches/equipment, as it applies.

- Cabling – HITS Fiber Optic Specifications

Backbone and patch cabling/patch panel will be one of two vendor types:

Note:  HHS standardized on Corning Cable Systems in 1999 but is open to PANDUIT Fiber Optic Products as an equal.

Corning Cable Systems or PANDUIT

Note:  A fibre run is required for every new communication room  home-run back to the Campus site computer room, unless otherwise determined at design stage.

If fibre path completely indoors and distance as the path taken is no greater than 984 feet (300 metres):

Twelve (12) strand cabling will be pulled from Campus Site Computer Room to each communication room which will consist of the following:

- 12 strand, 50 micron, tight buffered, laser optimized (OM3), 50/125, FT4, Aqua jacket

Rationale for laser optimized fibre deployment:

Current industry standard - capable of supporting 10 Gigabit speeds from communication room to computer room as needed in future for high bandwidth requirements.

If fibre path completely indoors and distance as the path taken is greater than 984 feet (300 metres):

Twelve (12) strand cabling will be pulled from Campus Site Computer Room to each communication room which will consist of the following:

- 900 micron, single mode, tight buffered fibre, FT4, yellow jacket

If any part of the fibre path is outside (aerial or underground), it will need to be loose tube or indoor/outdoor fibre for the entire distance from communication room to computer room.

Connectors:

LC-2-fibre type, no epoxy, prepolished

Fiber Optic Specifications continued

Patch Cords:

7 foot, two fibre, LC to LC – quantity 6 per communication room

15, 40 or 60 foot, two fibre LC or LC – quantity 6 per communication room (length to be determined at design stage)

Patch panels for each new room:

2U, 19” rack mounted shelf that will accept up to four 6-fibre LC connector housing panels complete with LC bulkheads.

Patch panels for Campus Site Computer Room (Data Center):

72 port patch panel(s), rack mountable, that will accept twelve 6-fibre connector housing panels (per patch panel) complete with LC bulkheads

The patch panels for both communication room and computer room are to be front facing, flip down lid style.  To be confirmed with HITS beforehand.

Fibre optic routing:

Fibre optic cabling will be run thru conduit as per:  Item 1.  Communication Standards

Fibre cabling to be home-run to Campus site computer room, unless otherwise specified

Fibre cabling to be home-run using dual conduit paths

Cable jacket to be FT4 rated thermoplastic except where otherwise indicated.

Cable jacket to be FT6 rated thermoplastic where any part of the cable is exposed

to an air return or air feed system.

Additional fibre cabling to be run between communication rooms for redundancy/failover:

- 6 strand, 50 micron, tight buffered, laser optimized (OM3), 50/125, FT4, Aqua jacket

To be determined at cabling infrastructure design stage.

Backbone cabling requirements for other departments is to be determined with the requestor and HITS.

7.  Cabling – Copper Specifications

CAT 6A Horizontal cabling will be PANDUIT:

Note:  HHS standardized on PANDUIT in 1999.  PANDUIT is the certified cabling partner to Cisco.

PANDUIT TX6A 10 GIG UTP Copper Cable with Matrix Technology – Part number PUR6A04BU-UG for riser rated cable, Part number PUP6AM04BU-UG for plenum rated cable.

Rationale for CAT 6A deployment -

Current industry standard - capable of supporting 1 Gigabit speed to the desktop device as needed in future for high bandwidth requirements.

Cabling type (HITS/Telecom/BioMed)

- 4-pair, #24 AWG, solid copper, CAT 6A, CSA PCC FT4 (CMR) unshielded, and or CSA PCC FT6 (CMP), twisted pair

- Potential shielded twisted pair requirement to be determined at design stage.

- Horizontal runs will be in accordance to CAT6A specifications and not exceed 295 feet (90 metres).

Patch cabling, face plates/jacks will be of one vendor type:

PANDUIT

Note:  HHS standardized on Cisco networking equipment in 1999.  PANDUIT is the Cisco certified cabling partner.

Jack type (ICT/Telecom/BioMed)

- 8-conductor, coloured modular jacks, Category 6A, T568A or 568B configuration (General/Juravinski – A, MUMC/Chedoke – B)

- Giga-Channel TX-6A Plus Series CJ6X88TG**

Colour jacket for horizontal cable, patch cable, jacks:

- Data/Voice: Blue (except for communication room pig tails – see below)

- BioMed:  White (if required for older installations)

Copper Specifications continued

Patch cables – (HITS/Telecom/Other):

- For device end:  10 foot, uniquely numbered (labeled at each end - 1..1, 2..2, continuum.)

- For communication room end:  7 foot, uniquely numbered (labeled at each end - 1..1, 2..2, continuum.)  For existing, older communication rooms - some longer patch cables are required (e.g.  15 or 20 foot). To be determined at cabling requirements stage.

- One patch cable for office end and one patch cable for closet end, for each horizontal cable run.

They will be solid or stranded conductor.  Each end terminated with 8 conductor, Category 6A, T568B RJ45 configuration modular plugs to match jacks.

Gigachannel TX-6A Plus Series Patch Cords UTP6ASD7**, UTP6ASD10**, UTP6ASD15**, UTP6ASD20**

Patch cables – Voice (Telecom):

If TDM phone:

- No patch cable required (provided with phone)

- For communication room end:  25 foot, uniquely numbered (labeled at each end - 1..1, 2..2, continuum.), cross connect CAT 6A, RJ45, grey colored pig tail cables (factory assembled) with RJ45 on one end to patch panel and the other end terminated to Cat 6 BIX block on wall (See Voice Trunk Cabling, pages 26, 27).

UTPSP25**.  Number of pig tail patch cables required will be determined by HITS/Telecom at design stage.

If VOIP phone:

- For device end:  10 foot, CAT 6A, RJ45 uniquely numbered (labeled at each end – 1..1, 2..2, continuum)

- For communication room end:  7 foot, CAT 6A, RJ45 uniquely numbered (labeled at each end - 1..1, 2..2, continuum.)

Wallplates/Surface Mounts (HITS/Telecom/BioMed):

- Quad or Duplex outlet, single gang, plastic, white complete with 2 label cards plus cover and blank inserts for unused port holes

- CFPL Series**

- To be placed with bottom side of wallplate, minimally 18” from floor OR above desk/counter (no higher than 4” above desk/counter) for easy access for servicing.

Copper Specifications continued

Faceplates (Modular Furniture Snap on Type):

Same as flush mount type except suitable for snapping into modular furniture raceways/knockouts.  Faceplates complete with extenders, as necessary

Faceplate/Jack for Wall Mount Telephone:

Stainless steel plate complete with Category 6 Keystone jack module and labels

PANDUIT – KWP6P Series**

Quantities as required for all of the above.  Determined at design stage.

Notes:

- Cabling is to be home-run from accessible office/area to communication room.

- No ceiling consolidation patch panel boxes.

- Cable jacket to be FT4 rated thermoplastic except where otherwise indicated.

- Cable jacket to be FT6 rated thermoplastic where any part of the cable is exposed

to an air return or air feed system.

- Cabling for common, multi user areas is to be pulled to different communication rooms for redundancy/failover purposes. To be determined at cabling infrastructure design stage.

.

Copper Specifications continued…

The following minimum clearances from electrical and heat sources are to be maintained when routing cables.

- Unit substations 10 m

- Power transformers (greater than 30KVA) 10 m

- Transformers 1.2 m

- Motors 1.2 m

- Switch gear (greater than 600V) 10 m

- Feeder cables (600V and above) 1 m

- Distribution cables (less than 600V) 750 mm

- Conduit (Enclosing 30A branch circuits) 300 mm

- Conduit (Enclosing 20A branch circuits) 75 mm

- Conduit (Enclosing 15A branch circuits) 65 mm

- Fluorescent luminaires 120 mm

- Pipes (gas, oil, water, etc.) 300 mm

- HVAC (equipment, ducts, etc.) 150 mm

Any deviation from cable routing shown on drawings to be approved by Engineer and documented on as-built drawings.

Additionally:

Do not strap cables to, or lay cables on, any length of conduit, pipe, ventilation duct or other building element not expressly installed for the purpose of cable support

.

When determining a cable routing pathway, give priority to air handling ducts, fire sprinkler pipes and electrical conduits.

8.  HITS UPS Specifications for Communication Rooms

UPS system will be of one vendor type:  APC

Note:  HHS standardized on APC in 1999.

There will be minimally one UPS in each communication room for HITS rack:

- APC Smart-UPS x 1 (or 2) – to be determined at design stage

- Along with 2 (or 4) PDU’s – to be determined at design stage

Product models:

UPS:								Receptacle:

APC  SMT 1500 (with APC 9630 network card)	             NEMA 5-15P

APC  SMT 2200 (with APC 9630 network card)	             NEMA 5-20P

APC  SURTA 3000XL (with APC 9630 network card)	 NEMA L5-30P

PDU:

APC AP9563 20A Rack Mount PDU

APC NET9RMBLK 15A Rack Mount PDU

Model type required for both UPS and PDU, to be determined at design stage.

Normal and Emergency power receptacles required for UPS models, vary as based on above.

The UPS size requirement will depend on the following factors:  number of switches required (based on number of total connections) and number of PoE (Power over Ethernet) switch ports required for potential VOIP phones and Wireless Access Points.

The UPS’/PDU’s are to be paid for by the project.

The UPS’/PDU’s are to be ordered by HITS.

The UPS’/PDU’s are to be installed by HITS.

The UPS’/PDU’s are to be for HITS/Telecom use only.

Note:  Any UPS requirements for Bio Med, Hospitality Network or other will need to be provided by them for the protection of their equipment.

9. Wireless Access Point (WAP) Surveying/Installation

- Surveying for determination of WAP locations will be performed by Compucom – HHS 3rd party network provider.

-     Surveying will be done for all areas.  Stairwells, elevators and outside of building may be included.

- Initial, best approach, conservative estimating for WAP location and quantities (and equal amount of cables required to be pulled by contractor) can be performed based on floor plan layouts

- Actual surveying cannot be performed until all construction walls are up and drop ceiling (with tiles) in place, doors, glass for doors and walls,  in order to determine the near final placement and locations for the WAP’s.

-     Final survey to be performed after furniture, staff moved in order to determine any fine tuning of WAP placement and locations (some may need to move).

- CAT 6A cabling for WAP’s will be brought back to communication room.

- WAP’s are to be installed by Contractor as per:

Site Survey Floor Plan Maps provided by HITS

Installation Guide provided – see page 16/17

- Survey Maps deliverable to Contractor will be sent in bmp or pdf format

- WAP’s are to be installed onto T-bar ceiling with AP exposed below drop ceiling (newer AP model) or as determined for hard ceiling

- WAP’s will receive power via CAT 6A cable from communication room switches (HITS provided).  Power not required in ceiling for WAP’s

- WAP’s will be provided by HITS

- Patch cables for patching WAP's to data cables will be provided by contractor.

- Outdoor WAPs, their protection and placement requirements to be determined at design stage

9.  Wireless Access Point Surveying/Installation continued

Wireless Access Point – Installation Guide

Installation instructions:

- Use electronic drawing sent along with this document, to identify installation location for each Wireless Access Point (WAP) identified in the table below.

- The WAP’s must be snapped onto T-bar ceiling, or as determined for hard ceiling

- Network horizontal cable will be laid to the determined communication room. Ensure that the length cable run does note exceed length specified by EIA/TIA-568 standard which is 295 feet (90 metres), end to end. Cabling for common, multi user areas are to be pulled to different communication rooms for redundancy/failover purposes. To be determined at cabling infrastructure design stage

- Network connection “surface mount” will be above drop ceiling (for newer model AP)

- Approximately 20 feet of extra cable is to be wrapped in a loop and left at each location as per the best guess paper survey locations noted.

- Mark (label) the wall plate using the standard HHS wall plate ID schema, as per diagram attached at the end of this document. See page 17.

- Wall plate ID label will be affixed to both surface mount and on the T-Bar of drop ceiling, (or to hard ceiling)

- Punch horizontal cable to CAT 6A patch panel in communication room.

- Install CAT 6A patch cable from surface mount to ETHERNET port on WAP.

- Enter corresponding Wall Plate ID for each WAP into the table below.

- Indicate if installation conforms 100% to installation instructions. Report any discrepancies in the Comment section (see table below).

- Forward the completed document to HITS contact who requested the installation, within 1 day after completion of the installation.

9.  Wireless Access Point Surveying/Installation continued

Sample form required to be returned from the Contractor listing wallplate ID’s, etc for each WAP Reference ID:

| WAP Reference ID (from Site Survey drawing) [HITS ] | Wall Plate ID [Engineering/ Contractor] | Install conforms to instructions (Yes / No) [Engineering] | Comment [Engineering] | WAP Name (UID) [Compucom] |
| --- | --- | --- | --- | --- |
| AP344 (ICU) |  |  |  |  |
| AP345 (ICU) |  |  |  |  |
| AP343 (CCU) |  |  |  |  |

The wallplate labeling schema for cabling is as follows:

XXXXXXXX-XXXX-XXXX which translates to:

8 alphanumeric maximum - 4 numeric - 4 alphanumeric

This schema is referencing the following:

OFFICE/AREA ROOM NO – COMM ROOM PATCH PANEL JACK NO – COMM ROOM I.D. NAME

Example - RM135-241-140

RM135-242-140

10. Labeling

The wallplate labeling schema for cabling is as follows:

XXXXXXXX-XXXX-XXXX which translates to:

8 alphanumeric maximum - 4 numeric - 4 alphanumeric

This schema is referencing the following:

OFFICE/AREA ROOM NO – COMM ROOM PATCH PANEL JACK NO – COMM ROOM I.D. NAME

Example - RM135-241-140

RM135-242-140

Note:  patch panel jack numbers 1 to 99 are to be labeled 001 to 099 at the wallplate and communication room ends.

See page 32 for Appendix A – Current Communication Rooms/ID’s

Note: Label font to be 10 or 12 pitch.  Determined with HITS beforehand for sample label provided by contractor.

No special characters, including dashes are to be used in the  OFFICE/AREA ROOM NO portion of the wallplate ID.   All capital letters.

Room/area portion part of wallplate ID is based on -  Owner’s Final (Wayfinding) Room Numbers (not Architectural Room Numbers).

Copper Horizontal Distribution Cabling

- Each cable leaving the communication room is to be labeled at both ends within 6” of termination point in sequential manner using labeling schema above.  No two cables leaving communication room shall share the same cable number.

- The patch panels numbers in the communication room will be a continuum.

e.g.  001 to 300.

- Therefore, beyond first 48 patch panel, every subsequent panel will be renumbered

049 to 096, 097 to 144, 145 to 192, …

- Labeling (Room Location) according to Owner’s Final Room Numbers (not Architectural Room Numbers).

- For any data cable that needs to terminate above drop ceiling with surface mount box (with patch cable down thru ceiling or wall), the wallplate ID must be on the surface mount box and on the ceiling T-bar beside WAP or Security Camera or on wall beside Clinical Camera.

10. Labeling continued

The communication room patch panel labeling layout is as follows:

Underneath or above each patch panel jack (dependent if top or bottom row of jacks) the OFFICE/AREA ROOM NO will be identified on the panel.

10.  Labelling continued

The office/area wallplate labeling layout is as follows:

Labels need to be placed on left and right side of jacks regardless of 2 gang or 4 gang jack.  One unique label per jack.

Labeling System:  PANDUIT or approved equal (Brother P Touch Labels Not Accepted)

If required, labeling for Bio Med, Hospitality Network, other - needs to be determined with respective departments and HITS.

11. Installer Approval/Certification

Approved cabling installer/contractor must be a current approved Panduit Certified Installer (PCI) in good standing. Each Panduit Certified Installer must supply their PCI Certificate as part of their submittal with their Price/RFQ package. The Panduit Certified Installer can access and download their “PCI Certificate” through the Panduit Partner ONE HUB Portal. The approved cabling installer/contractor will provide a PANDUIT “Certification” System Warranty (25 year) upon completion of the project.  The PCI will perform all of the following during installation:  Pull cables, terminate cables, test cables & label cables.  All cable test results and Certification forms must be submitted to Panduit’s warranty department via the Panduit Partner ONE HUB Portal.  This is required by the Panduit Certified Installer in order to provide the PANDUIT “Certification” System Warranty (25 year).

12.  Installation Warranty

-    Approved cabling installer/contractor will provide PANDUIT “Certification” System Warranty (25 year) upon completion of the install/project.

- Fulfill all of PANDUIT’s Warranty/Certification registration requirements.  Prepare and submit electronically all necessary certification forms/documentation and cable test results  to PANDUIT’s warranty department via the Panduit Partner ONE HUB Portal.

-    Submit Warranty certificates at conclusion of installation to Hamilton Health Sciences -  Capital Development/Engineering and HITS Department contacts assigned to the project install.

Installer Approval/Installation Warranty  for other type cabling systems to be determined by the department.

13. Documentation

Submit shop drawings for the following items:

- Voice/Data jacks/faceplates

- Horizontal cabling (data/voice)

- Horizontal patch panels

- Backbone (fibre/voice trunk) cabling (data/voice)

- Backbone (fibre/voice trunk) patch panels/Bix blocks

- Equipment & Cabling racks

- Labelling

Submit upon completion of data cabling installation on CD in AutoCAD format all details regarding the installation:

- Comm room location

- Voice/Data cabling routing

- Voice/Data wallplate outlet locations on floor plan maps complete with wallplate ID's

Submit labeling samples for patch panel jacks, wallplates, horizontal cables, and patch cables for approval prior to commencing work.

14.  Execution – Co-ordination

- Co-ordinate all cabling work with the HHS HITS/Telecom/BioMedical /Engineering/Security/Multi-Media- Services.

- Prior to start of work, Contractor to present methodology/process for pulling, terminating, testing and labelling cables – CAT6A, fiber optic, voice trunk, pig tails.

Documentation for other type cabling systems to be provided as requested by the department.

15.  Testing and Verification

Permanent Link Horizontal CAT6A cabling to be tested to EIA/TIA 568B Category 6A Standard for the following:

- Circuit/Cable identification

- Wire Map

- Length

- Impedance

- Resistance

- Capacitance

- Near End Cross Talk

- ACR, PS ACR

- PSNEXT

- ELFEXT

- PSELFEXT

- Return loss

Testing to be done with comm. room lights on and rack grounded.

Fibre Optic cabling to be tested for the following:

Test each strand for dB loss.

Test each cable strand with light source meter compliant with TIA/EIA-568-B Standard

Test each cable whose length is in excess of 400 feet (122 metres) with an Optical Time Domain Reflectometer per TIA/EIA 455-61

If a fault or sub-standard condition is discovered during inspection and testing:

The dates on which such conditions were first noted and ultimately corrected shall be entered in the log.

The cause shall be identified and corrected.

The affected tests shall be repeated for that strand.

Any previous tests where the results could have been affected by the corrective action shall also be repeated.

Document results for each strand in CD format.  Format shall include tables indicating the expected results and the actual results.

Testing/Verification for other type cabling systems to be provided as required by the department.

- Testing and Verification continued

Provide Permanent Link  testing for each CAT 6A cable installed per TIA/EIA 568B testing standards

Use Micro Test Omniscanner or Fluke Meter DSP4300 or higher

If a fault or sub-standard condition is discovered during inspection and testing:

The dates on which such conditions were first noted and ultimately corrected shall be entered in the log.

The cause shall be identified and corrected.

The affected tests shall be repeated for that circuit.

Any previous tests where the results could have been affected by the corrective action shall also be repeated.

Document results for each cable and patch cord in CD format.  Format shall include tables indicating the expected results and the actual results.

Copper Backbone Cabling (Voice Trunk):

Test for:

Continuity/Opens

Shorts

Grounds

Polarity

Length

16. Voice Trunk Cabling

Bix Mounts/Connectors (Voice)

Note:  HHS is standardized on the following vendor types:

NORDX/CDT QMBBIX Series

250-pair mounts (or as agreed upon with Telecom) complete with 10 BIX Connectors and 5 designation strips and labels

Mounts suitable for wall mounting

Mounts complete with distribution rings for wire management.

Label BIX connector designation strips using Owner’s Final Room Numbers (not Architectural Room Numbers).

Copper Cabling (Voice Trunk)

Pair count (quantities as required), #24 AWG, solid copper, CSA PCC FT4 (CMR) jacket

Superior ESSEX AR Series or approved equal

Provide BIX mounts in quantities indicated filled complete with BIX connectors and designation strips for backbone and horizontal cabling terminated in communication rooms and Main Telephone Room.

Bix Mount for Cat 6 pig tails (from comm rack to wall board)

Giga Bix Mount 12 connector    AX101472
Giga Bix Connector 6 port    AX101447
Giga Bix Wire Guard AX101486
Giga Bix Designation strip  AX101483
Kit containing all of the above for 72 ports AX101470.  Quantities as required.

Bix mount for 25, 50, 100, 250 pair voice trunk cable

Bix 10a Mount 250 pair A0270164
Bix 1A connector  A0266828
Bix 1A4 connector A0393146

See below pictures for Bix block/pig tails at wallboard and rack.

Document results in CD format.  Format shall include tables indicating the expected results and the actual results.

- Voice Cabling continued - Cat 6 Bix Mount for pig tails

- Wireless Guidelines

As per new standards for HHS connectivity for computing devices/phones:

The following devices will be or will have the potential to become wireless:

Includes:

- all HHS approved handheld Laptops

- all HHS approved handheld PDA'S

- all HHS approved handheld Tablets

- all HHS approved desktop and handheld IP phones

- all HHS approved BioMedical mobile pumps for infusion data collection use

- all HHS, HITS supplied, thin client computers (currently Wyse)

The following devices will continue to be wired:

Includes:

- all HHS approved networked printers

- all HHS approved embossers (or the like)

- all HHS approved 3rd party equipment (GE Med, Siemens, Toshiba, Kodak, etc)

- all HHS approved lab instruments

- all HHS, HITS supplied, desktop p.c.'s for regular, standard suite of applications use

- all HHS, HITS supplied, desktop p.c.'s for high resolution

- (e.g. PACS) applications, web browser viewing use

- all HHS approved desktop p.c.'s for specific (e.g. PACS GE Centricity) review stations use

- all HHS approved bedside p.c.’s for patient infotainment applications use

- all HHS approved BioMedical p.c.’s for real time patient monitoring use

- all HHS approved Wireless Access Points

- all HHS approved desktop phones (as required)

- HHS Cabling Direction for HITS/Telecom/Patient Monitoring/other

HHS Cabling Direction for HITS/Telecom/Patient Monitoring/other

There will be a requirement for one CAT 6A data line for every one of the following types of devices:

Includes:

P.C.’s

All Printers (including multifunction laser, thermal)

Embossers

Lab instruments

PACS Centricity Review stations

3rd party equipment (e.g. Radiology)

Wireless Access Points

Observation cameras

Patient Monitoring

Kiosks

Fax machines

Multi-Media equipment

Phones

Signage boards

Donor boards

Debit/Cash Register systems

Note 1:  The printer/fax may be combined and therefore requiring 2 CAT 6A data lines (1 for data and 1 for voice).

Note 2:  If VOIP phone, regular p.c. to connect to back of phone (where applicable)

Note 3:  If TDM phone, regular p.c. to connect direct to wallplate or potentially be made wireless (if thin client computer)

Note 4:  As part of department moves from one building/wing/floor/area to another building/wing/floor/area, any TDM phones will become wired or wireless VOIP.

18. HHS Cabling Direction for HITS/Telecom/Biomed/other continued

- Power Requirements for Devices

Emergency power (not limited to the following), will be required, subject to approval process):

Patient Monitoring

All Printers (including multifunction laser, thermal)

Embossers

PACS Centricity Review stations

3rd party equipment (e.g. Radiology)

Fax machines

Important p.c.’s (e.g. Ward Clerk/Reception p.c.)

Other devices (e.g.  Acudose Cabinets)

- Appendix A - Current HHS Communication Room Locations/ID’s

| Site | Current Closet | old closet splice point | Building | Floor | Location |
| --- | --- | --- | --- | --- | --- |
| MUMC | 1C7 |  | Main | 1st | Red Area 1C7B |
| MUMC | 232 |  | Main | 2nd | Red Area 2G32C |
| MUMC | 311 |  | Main | 3rd | Red Area 3D11C |
| MUMC | 4D8 |  | Main | 4th | Red Area 4D8C |
| MUMC | 3GC |  | Main | 3rd | Red Area 3G51 |
| MUMC | 3C7 |  | Main | 3rd | Purple Area 3H7 |
| MUMC | 3N5 |  | Main | 3rd | Blue Area 3N6C |
| MUMC | 2N5 |  | Main | 2nd | Blue Area 2N5 |
| MUMC | P10 |  | Main | 1st | Blue Area 1P40 |
| MUMC | 2QC |  | Main | 2nd | Yellow Area 2Q36C |
| MUMC | 2S3 |  | Main | 2nd | Yellow Area 2S3 |
| MUMC | 329 |  | Main | 3rd | Yellow Area 3X29 |
| MUMC | 411 |  | Main | 4th | Yellow Area 4W11B |
| MUMC | 336 |  | Main | 3rd | Yellow Area 336 |
| MUMC |  | 2-33C to 232 | Main | 2nd | beside shaft 33 |
| MUMC |  | 3-57c to 329 | Main | 3rd | beside shaft 57 |
| MUMC |  | 2-38C to 2S3 | Main | 2nd | beside shaft 38 |
| MUMC |  | 3-54C to 311 | Main | 3rd | beside shaft 54 |
| MUMC |  | 2-34C to 232 | Main | 2nd | beside shaft 34 |
| MUMC |  | 4-48C to 411 | Main | 4th | beside shaft 48 |
| MUMC |  | 2-35C to 232 | Main | 2nd | beside shaft 35 |
| MUMC |  | 4-33C to 4D8 | Main | 4th | beside shaft 33 |
| MUMC |  | 2-48C to 2S3 | Main | 2nd | beside shaft 48 |
| MUMC |  | 3-74C to 3C7 | Main | 3rd | beside shaft 74 |
| General | BST |  | Main | Basement | Outside of Pharmacy Storage |
| General | 1Y1 |  | Main | 1st | Outside of Pop Health |
| General | 1EL |  | Main | 1st | Across from Pharmacy |
| General | 1PT |  | Main | 1st | Beside Pathology |
| General | 2RD |  | Main | 2nd | Across from Pod 3 |
| General | 3SL |  | Main | 3rd | Outside of Blood Bank |
| General | 4WS |  | Main | 4th | Beside 4 West Nurse Station |
| General | 7WS |  | Main | 7th | Beside 7 West Nurse Station |
| General | 3UP |  | North Wing | 3 Upper | Beside Stairwell |
| General | 6NT |  | North Wing | 6th | Beside Housekeeping Room |
| General | 2EW |  | East Wing | 2nd | Beside Old Vault Room |
| General | 4EW |  | East Wing | 4th | Nearby Elevators |
| General | BMC |  | McMaster Wing | Basement | Across Theater Auditorium |
| General | 4MC |  | McMaster Wing | 4th | Beside Room 423 |
| General | RMP |  | Parking Ramp | Level B | Outside of RIA Lab |
| General | JRS |  | Junior Residence | Basement | Mechanical Room |
| General | 3HU |  | HIU | 3rd | Beside Waiting Area |
| General | MSN |  | 293 Wellington | North Side | off hallway, outside of ICT |
| General | MSS |  | 293 Wellington | South Side | off main hallway |
| General | R1S |  | Rehab | South Side | off hallway |
| General | R2S |  | Rehab | South Side | off hallway |
| General | R3S |  | Rehab | North Side | off hallway |
| General | R1N |  | Rehab | North Side | off hallway |
| General | R2N |  | Rehab | North Side | off hallway |
| General | R3N |  | Rehab | North Side | off hallway |
| General |  | 1ST ELEV to 1EL | Main | 1st | Beside Pharmacy |
| General |  | 2 RAD to 2RD | Main | 2nd | off hallway, across Pod 3 |
| General |  | 3 O.R. to 3SL | Main | 3rd | off hallway, across Patient Holding |
| General |  | 5TH MAC to 4MC | McMaster | 5th | old Linen Chute |
| General |  | 7 WEST to 7WS | Main | 7th | off hallway, beside power closet |
| General |  | 4 WEST to 4WS | Main | 4th | off hallway, beside power closet |
| General |  | 7TH MAC to 4MC | McMaster | 7th | old Linen Chute |
| General |  | 2ND MAC to BMC | McMaster | 2nd | old Linen Chute |
| General |  | 3 ICU to 2RD | Main | 3rd | off hallway, beside power closet |
| General |  | 3 ELEV to 3SL | Main | 3rd | off hallway, across service elevator |
| General |  | 2 E.R. to 1Y1 | Main | 2nd | off hallway, across Cardiac Suite |
| General |  | 1ST PATH to 1PT | Main | 1st | off hallway, across Forensic offices |
| General |  | 1ST STRS to BST | Main | 1st | off hallway, across Nutrition Services |
| General |  | BSMT to BST | Main | Basement | off hallway, outside Pharmacy storage |
| Juravinski | C90 |  | 90 (E/F) | 1st | Beside Telecom Room |
| Juravinski | 490 |  | 90 (E/F) | 4th | Across from Elevators |
| Juravinski | G60 |  | 60 (G) | Ground | Off Hallway to JCC |
| Juravinski | 260 |  | 60 (G) | 2nd | Beside Reception Desk |
| Juravinski | 140 |  | 40 (M) | 1st | Behind Elevators |
| Juravinski | 540 |  | 40 (M) | 5th | Across from Elevators |
| Juravinski | G15 |  | 15 (H) | Ground | Beside Maintenance Shop |
| Juravinski | 215 |  | 15 (H) | 2nd | Across from Elevators |
| Juravinski | BLR |  | 25 (K) | 2nd | Beside Control Room |
| Juravinski | CON |  | Concession Ramp | Mechanical Room | Beside Parking Office |
| Juravinski | POP |  | Poplar Ramp | Mechanical Room | 1st floor |
| Juravinski | J0S |  | new build | Level 0 South | Off main hallway |
| Juravinski | J1S |  | new build | 1st South | Off main hallway |
| Juravinski | J3S |  | new build | 3rd South | Off main hallway |
| Juravinski | J4S |  | new build | 4th South | Off main hallway |
| Juravinski | J0N |  | new build | Level 0 North | Off main hallway |
| Juravinski | J1N |  | new build | 1st North | Off main hallway |
| Juravinski | J3N |  | new build | 3rd North | Off main hallway |
| Juravinski | J4N |  | new build | 4th North | Off main hallway |
| Juravinski | J0E |  | new build | Level 0 South East | Off hallway outside of OR rooms |
| Juravinski | J1E |  | new build | 1st South East | Off hallway inside DI office area |
| Juravinski | J3E |  | new build | 3rd South East | Off hallway inside Clinical Teaching Unit offices |
| Juravinski | J0W |  | border of new build/old 90 | Level 0 West | Off hallway, across E/F Elevators |
| Juravinski | J1W |  | border of new build/old 90 | 1st West | Off hallway, across E/F Elevators |
| Juravinski | J3W |  | border of new build/old 90 | 3rd West | Off hallway, across E/F Elevators |
| Juravinski | J4W |  | border of new build/old 90 | 4th West | Off hallway, across E/F Elevators |
| Juravinski |  | 1ST 40 to 140 | 40 (M) | 1st | inside Electrical Room beside Elevator |
| Juravinski |  | GRND 15 to G15 | 15 (H) | Ground | inside CSR Holding Area |
| Juravinski |  | 2ND 15 to 215 | 15 (H) | 2nd | other side of wall to current closet |
| Juravinski |  | 2ND 60 to 260 | 60 (G) | 2nd | on side wall within current closet |
| Chedoke | HOB |  | Holbrook | Basement | Telecom Room |
| Chedoke | WRD |  | Wilcox | Basement | Room within B06 |
| Chedoke | WC2 |  | Wilcox | 2nd | By Elevators |
| Chedoke | CEN |  | Central | 3rd | Within Office Area |
| Chedoke | STH |  | Southam | 2nd | Off Hallway |
| Chedoke | WQ2 |  | West Quarters | 2nd | Within Office Area |
| Chedoke | CBO |  | Ewart Angus | Basement | In Electrical Room |
| SPH | LES |  | Main Building | Lower East | by Classroom B |
| SPH | LWS |  | Main Building | Lower West | by entrance to South Wing |
| SPH | 1ES |  | Main Building | 1st East | beside Dental Clinic |
| SPH | 3WS |  | Main Building | 3rd West | near 3 West |
| SPH | PVS |  | Pavilion | 2nd floor | by Elevators |
| SPH | PVN |  | Pavilion | 2nd floor | inside secured patient area |
| 688 Concession | 688 |  | Main building | 2nd floor | near back entrance staircase to 2nd floor |
| 529 Concession | 529 |  | Main building | 1st floor | near back entrance |
| West End Clinic | WEC |  | Main building | 1st floor | inside and back of UCC |
| 40 Wellington | WEL |  | Main building | Main floor | inside of BAHT area |
| Barton Lot | BPL |  | Barton Parking Lot | Cabinet | Inside of cabinet |
| RJCHC | RJ1W |  | RJCHC | 1st | Off main hallway, West side |
| RJCHC | RJ2W |  | RJCHC | 2nd | Off main hallway, West side |
| RJCHC | RJ3W |  | RJCHC | 3rd | Off main hallway, West side |
| RJCHC | RJ4W |  | RJCHC | 4th | Off main hallway, West side |
| RJCHC | RJ4E |  | RJCHC | 4th | Off main hallway, East side |
| WLMH | AGB |  | Alexander Globe | Main floor | By door entrance |
| WLMH | BCE |  | Basement Central | Basement floor | Inside DI |
| WLMH | BFR |  | Basement Front | Basement floor | Inside old Accounting |
| WLMH | DPV |  | Deer Park Villa | Main floor | Off hallway |
| WLMH | GCN |  | Ground Central | Main floor | Off hallway |
| JCC | CC0S |  | By South Elevators | Level 0 | Off hallway |
| JCC | CC0N |  | By North Elevators | Level 0 | Off hallway |
| JCC | CC1S |  | By South Elevators | Level 1 | Off hallway |
| JCC | CC1N |  | By North Elevators | Level 1 | Off hallway |
| JCC | CC2S |  | By South Elevators | Level 2 | Off hallway |
| JCC | CC2N |  | By North Elevators | Level 2 | Off hallway |
| JCC | CC3S |  | By South Elevators | Level 3 | Off hallway |
| JCC | CC3N |  | By North Elevators | Level 3 | Off hallway |
| JCC | CC4S |  | By South Elevators | Level 4 | Off hallway |
| JCC | CC4N |  | By North Elevators | Level 4 | Off hallway |

21. Existing Cabling De-commissioning (Renovation)

For each and every cable that is required to be decommissioned, the following is required:

- HITS notified of the wallplate ID

- Horizontal cable tested first to ensure end to end connectivity before decommissioning

- Horizontal cable removed from the backside of communication room patch panel, corresponding jack

- Cable is completely removed from office/area back to communication room (or minimally cut above ceiling) – please consult Engineering

- Wallplates and labels removed from wall

i.e.:

office end - RM135-241-140

comm. room end – backside of patch panel for jack 241 (5th patch panel, punch down jack 45)

This work needs to be accounted for in any renovation project that entails removing existing cabling.

Decommissioning for Telecom cabling is to follow suit per the above as much as possible.  Cabling may be going to rack or wall mount Bix blocks.

22.  Relocating an existing HITS communication room

Relocating an existing HHS HITS communication room

Requires the project/contractor to do the following items:

- determine all wallplate locations (cables) that go back to the comm room and plot on floor plan with wallplate ID’s, including wireless access point locations (if existing)

b.    build new comm room, as per HHS Infrastructure spec

c.    pull new CAT 6A cables from locations (as required) back to new comm rooms, given 295 feet (90 metre) length spec

d.    cutover ‘active’ wallplates with computing/telephony devices from existing wallplate to new wallplate (as required) with HITS/Telecom (3rd party) assistance

e.    remove all old wallplates; and cabling right back to the existing comm room, as per HHS Infrastructure spec

f.   provide new patch cables (quantities as required) for new or existing comm room or both, as per HHS Infrastructure spec

g.  install new rack system build as per HHS infrastructure spec

h.  install voice trunk cabling (as required)

i.  provide new patch panels/wire managers (quantities as required), as per HHS Infrastructure spec

Items for costing:

- Comm room build which includes rack system (with CAT 6A patch panels), fibre optic pull (with fibre patch panels), UPS

B.  Average cost for new cable pull (includes terminate, test and label)

C.  Cost to determine all existing wallplate locations (plus time to map onto floor plan)

D.  Cost to cutover all ‘active’ wallplates with computing/telephony devices

E.  Cost for patch cables

- Average cost to remove old cable

Relocating an existing HITS communication room continued

- Cost to install, configure switches, activate and cross-connect switch

H.  Voice trunk cabling from comm room to Telephone Room, plus pig tail cabling within comm room

if converting p.c. to wireless instead:

I.  cost of wireless card

J.  cost of pulling cable/installing WAP

The project is to budget for the following:

- Contractor time and material

- HITS/Telecom (3rd party) time

- HITS material (potential wireless cards)

- Identify ongoing operating costs

*** The project would be impacting clients as follows***:

- disruption to client community to pull new cables to existing wallplate locations and ceilings (for WAP's)

- service interruption to client community and computing/telephony devices to cutover from old to new wallplates (cables) or install wireless card

- disruption to client community to remove existing wallplates and cabling back up to ceiling

Run rate to cutover ‘active’ wallplates with computing/telephony devices from old to new wallplates:

15 minutes? per computing device @ 4 devices per hour times 7 hours? = 28 per day?

or

30 minutes? per computing device @ 2 devices per hour times 7 hours? = 14 per day?

23. Cabling practices for MUMC – re: HHS vs University

For any cabling at MUMC, regardless if it is for HHS or University staff and devices, if it is within HHS physical space, it is to be cabled to HHS communication room.

There is to be no cabling of University staff and devices, to University communication room, if it within HHS physical space.

This also applies to Wireless Access Points.  There are to be no University WAPs within HHS physical space.

Capital Development/Engineering to consult with HITS for HHS space vs University space understanding at the time of project request.

24. New Building – construction requirements

For new buildings, the following must be included:

- Multiple pathways (conduits) to the base building (containing the central locations for HITS and Telecom) of the site.  Two entrance facilities to new building, located at opposite ends of building.

- Multiple pathways (conduits) to the street for connectivity to 3rd parties (Bell, Atria, etc).  Two entrance facilities to new building, located at opposite ends of building.

- All communication rooms are to be minimally 300 square feet. Room layout for racks, wallboard BIX blocks, etc, to be as per noted previously in this document (communication room layout).  Final sizing and layout to be determined at time of design stage with all requirements of room understood.

- Communication rooms must be situated off of main hallways, not sub-hallways within clinical/staff occupied space.  No washrooms situated beside or above.  The number of communication rooms required is to be determined at design stage.

- Multiple pathways (conduits) to the floors for connectivity to 3rd parties (eg. Bell) for Hi Speed internet services that may be required separate from the HHS data network and/or for single business telephone lines that may be required.