Summary of Asbestos Locations Hamilton Health Sciences, McMaster Site

***For Full Asbestos Management Program Document See Engineering Supervisor or Project Manager***

**Revised February 3, 2020**

**IF AREA OR MATERIALS ARE NOT IN THIS INVENTORY**

**WE ASSUME IT HAS ASBESTOS MATERIAL UNLESS TESTING PROVES OTHERWISE**

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | **MM Level** |  |  |  |
| **Material** | **Locations** | **Approx. Quantity** | **Sample Number(s)** | **Result (if ACM)** |
| Tar insulation – Non-friable | Chilled water, domestic water lines | n/a | 004a | Chrysotile |
| Tar patches over fibreglass pipe insulation – Non-friable | Chilled water, domestic water lines | n/a | 16162-MUMC-ASB-03a | Chrysotile |
| Parging cement – Friable | Pipe fittings  Chilled water storage tanks (purple) | 200 sf | 002a & 005a  008a | Chrysotile  Chrysotile |
| Brown Duct Mastic | Supply and Return Air Ducts | n/a | 16162-MUMC-ASB-05a | Chrysotile |
| Drywall joint compound – Non-Friable | Quadrant dividing walls, storage rooms, corridors and miscellaneous | 100% | various | Chrysotile |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | **Shafts** |  |  |  |
| **Material** | **Locations** | **Approx. Quantity** | **Sample Number(s)** | **Result (if ACM)** |
| ACM fireproofing - Friable | shafts 36, 43, 45, 48, 56, 63 and 68 (and above 4M in all other shafts) | n/a | n/a | Chrysotile |
|  | -Interface with interstitial spaces: where some beams exit the interstitial spaces (testing of suspect material is required)  Removals in Clean shafts (33, 34, 35, 37, 38, 44, 46, 47, 53, 54, 55, 57, 58, 64, 67, 73, 74, 75, 76, 77 & 78) have some residual ACM | n/a | n/a | Chrysotile |
| Parging cement - Friable | the majority of pipe fittings | n/a | n/a | Chrysotile |
| Tar insulation – Non-friable | Chilled water, domestic water lines | n/a | 004a | Chrysotile |
| Tar patches over fibreglass pipe insulation – Non-friable | Chilled water, domestic water lines | n/a | 16162-MUMC-ASB-03a | Chrysotile |
| Drywall joint compound- Non-Friable | Walls | n/a | n/a | Chrysotile |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | **Glass shafts** |  |  |  |
| **Material** | **Locations** | **Approx. Quantity** | **Sample Number(s)** | **Result (if ACM)** |
| Parging cement – Friable | Roof drains and misc fittings | n/a | n/a | Chrysotile |
| Sprayed Fireproofing - Friable | Non-asbestos Cementitious (hard coat)  **Asbestos containing base-coat** | n/a | n/a  **2013 Sampling** | Non-asbestos  **Chrysotile** |
| Tar insulation – Non-friable | Chilled water, domestic water lines | n/a | 004a | Chrysotile |
| Tar patches over fibreglass pipe insulation – Non-friable | Chilled water, domestic water lines | n/a | 16162-MUMC-ASB-03a | Chrysotile |
| **Except:** | -Structural steel in shaft 26 on level 1 and 1M levels  -Structural steel in -shafts 65 and 89 at 5M & 6 levels  -Interface with interstitial spaces: where some beams exit the  interstitial spaces (analysis of suspect material is required)  -Structural steel in shaft 66 on level 5 and 5M  -Structural steel in 44, 47, 74 & 77 had removals of spray-on above  level 6 & are bare steel; levels 5, 5M & 6 of these glass towers  contain ACM | n/a | 021 a-c | Chrysotile |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | **Exterior Stairwells** |  |  |  |
| **Material** | **Locations** | **Approx. Quantity** | **Sample Number(s)** | **Result (if ACM)** |
| Parging cement - Friable | Roof drains and misc fittings | n/a | n/a | Chrysotile |
| Sprayed Fireproofiing - Friable | Non-asbestos Cementitious (hard coat) Top Coat  Asbestos containing base-coat | n/a | n/a  2013 Sampling | Chrysotile |
| **Except:** | -Interface with interstitial spaces: where some beams exit the  interstitial spaces (testing of suspect material is required) | n/a | 021 a-c | Chrysotile |
| Drywall joint compound – Non-Friable | Walls | n/a | n/a | Chrysotile |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | **Parking Garages** |  |  |  |
| **Material** | **Locations** | **Approx. Quantity** | **Sample Number(s)** | **Result (if ACM)** |
| Texture finish - Friable | Blue area corridor to morgue  Yellow area-south/east corner  East exit and tunnel from Elevator 22 | 1,000 sf  1,500 sf  7,000 sf | 056a  012a  HHS (Sept 2012) | Chrysotile  Chrysotile  Chrysotile |
| Parging cement - Fribale | -Hearse loading area  -mechanical rooms | 20 fittings | n/a  n/a | Chrysotile  Chrysotile |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | **Interstitial Spaces**  **1M to 4M** |  |  |  |
| **Material** | **Locations** | **Approx. Quantity** | **Sample Number(s)** | **Result (if ACM)** |
| Parging cement - Friable | The majority of pipe fittings | n/a | n/a | Chrysotile |
| Sprayed fireproofing- Friable | All areas, encased  **(except in portions of M1Q2 above MDRD which contains a fiberous non-asbestos fireproofing)** | n/a | n/a | Chrysotile |
| Tar insulation – Non-friable | Chilled water, domestic water lines | n/a | 004a | Chrysotile |
| Tar patches over fibreglass pipe insulation – Non-friable | Chilled water, domestic water lines | n/a | 16162-MUMC-ASB-03a | Chrysotile |
| Brown Duct Mastic | Supply and Return Air Ducts | n/a | 16162-MUMC-ASB-05a | Chrysotile |
| **Except:** | The underside of the beams where the beam abuts the  double drywall See Appendix “W” MUMC AMP For details | n/a | n/a | Chrysotile |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | **Level 5M** |  |  |  |
| **Material** | **Locations** | **Approx. Quantity** | **Sample Number(s)** | **Result (if ACM)** |
| Parging cement- Friable | all pipe fittings | n/a | n/a | Chrysotile |
| Sprayed fireproofing - Friable | All areas-not encased, debris on all surfaces  Access restricted to Type 2 PPE – Only Hatch and landing areas have been encased | n/a | n/a | Chrysotile |
| Tar insulation – Non-friable | Chilled water, domestic water lines | n/a | 004a | Chrysotile |
| Tar patches over fibreglass pipe insulation – Non-friable | Chilled water, domestic water lines | n/a | 16162-MUMC-ASB-03a | Chrysotile |
| Brown Duct Mastic | Supply and Return Air Ducts | n/a | 16162-MUMC-ASB-05a | Chrysotile |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | **TeleLift Shaft Within Interstitial Space – Runs Vertically** |  |  |  |
| **Material** | **Locations** | **Approx. Quantity** | **Sample Number(s)** | **Result (if ACM)** |
| Sprayed fireproofing - Friable | All areas-not encased, debris on horizontal surfaces  Access restricted to Type 2 PPE | n/a | n/a | Chrysotile |
|  | **Level 6** |  |  |  |
| **Material** | **Locations** | **Approx. Quantity** | **Sample Number(s)** |  |
| Parging cement - Friable | all pipe fittings | n/a | n/a | Chrysotile |
| Tar insulation – Non-friable | Chilled water, domestic water lines | n/a | 004a | Chrysotile |
| Tar patches over fibreglass pipe insulation – Non-friable | Chilled water, domestic water lines | n/a | 16162-MUMC-ASB-03a | Chrysotile |
| Brown Duct Mastic | Supply and Return Air Ducts | n/a | 16162-MUMC-ASB-05a | Chrysotile |
| Sprayed fireproofing - Friable | All areas encased, except Substation rooms, Blue and Purple Eleator Rooms, Service Elevator Rooms, DG 1 & 2.  3/4 of DG 5, 6, 8 are encased, all of DG 3 is encased | n/a | n/a | Chrysotile |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | **Building Exterior** |  |  |  |
| **Material** | **Locations** | **Approx. Quantity** | **Sample Number(s)** |  |
| Exterior Building Caulking – Grey | MUMC Front Canopy – Assumed to be present throughtout the building exterior unless sampling proves otherwise | n/a | S-009b | Chrysotile |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | **Level 1 to 4** |  |  |  |
| **Material** | **Locations** | **Approx. Quantity** | **Sample Number(s)** | **Result (if ACM)** |
| Floor tiles – Non-Friable | Refer to Appendix IV – Attached | n/a | n/a |  |
| Vinyl sheet flooring – Paper Backing is Friable | Refer to Appendix V – Attached | n/a | n/a |  |
| Carpet – Non-Friable | Assume all Carpet adhesive contains Asbestos | n/a | n/a | Assumed asbestos type other than Chrysotile |
| Acoustic ceiling tiles – Non-Friable | Throughout entire building | n/a | n/a | Chrysotile |
| **Except:** | Level 1-Cafeteria, 1M Shipping/Receiving Offices (IT), Garbage  Dock (IT), MDRD, Stores (IT/IE), & Pharmacy (IE) Level 2 Main Entrance  Red Elevators to Yellow Elevators straight through Main Lobby | n/a | n/a |  |
| Fumehoods, lab cabinets  fumehood exhausts – Non-Friable  *Any doubt as to the*  *makeup of the hood lining*  *it is to be considered as*  *Asbestos until testing*  *proves otherwise* | * 1P8 FH#1 & #2 * 2N49 FH#1, #2 & #3 * 2N13 FH # HLMP1941 * 3N38 FH#1, #2 & #5 * 4H3 FH #74-6F * 4N71 FH#2 * 4N75 FH#2 & #3 * 4N76 FH#1 * 4N68 FH#1 * 4H8 FH#1 * 4H9 FH#1 | n/a | n/a | Transite |
| Under sink chase pipes,  conduit, – Non-Friable etc *Any service*  *pipe or conduit through*  *the floor not listed or*  *labeled as Asbestos free is*  *to be considered as*  *Asbestos other than chrystotile until testing*  *proves otherwise* | 2V8-2, 2V8-3  2N49-1, 2N49-3, 2N49-5, 2N49-6  2N22-1, 2N22-2, 2N22-4, 2N22-6  **Under workbench #***5* 2N22  2N13-1, 2N13-3, 2N13-4, 2N13-5, 2N13-6, 2N13-7  2N28-5, 2N38-8  3H45-1,3H45-2, 3H45-3, 3H45-5  4 | n/a | n/a | Assumed Asbestos Tyoe other athan Chrysotile |
| Undersink Black Sink Mastic | Throughout building in lab bench sinks – underside of sink coated with black asbestos-containing mastic | n/a | 16162-MUMC-ASB-07a | Chrysotile |
| Window boxes  systems – Non-Friable *are*  *to be considered as*  *Asbestos containing until*  *Testing proves otherwise* | All outer / exterior wall offices and patient rooms that contain a window box system | n/a | n/a | Assumed Asbestos Tyoe other athan Chrysotile |
| Paper Insulation on Elevator Switches - Friable | All elevators | ? | Suspected | Assumed Asbestos Tyoe other athan Chrysotile |

**APPENDIX IV - Vinyl floor tiles – Non Friable**

Twenty-one visually distinct types of vinyl floor tiles were sampled throughout the building, as follows:

| Tile Size (inches) | Colour/Pattern | Locations | Sample Numbers | Asbestos |
| --- | --- | --- | --- | --- |
| 12” x 12” | Green with white fleck | **Purple Rooms** Purple L1 Corridor, **Blue Rooms** 2N39, 2N45, 2N47, 2N52-56, 2T1E-1G, 2TC4, Room 3U10, **Red Rooms** L1 corridors, 3D1**,** 3D5, 4B1A-21, **Yellow Rooms** 1S1A, 2Q32-36, 2Q38-41, 2R29, 2RC1 | 013a | Chrysotile |
| 12” x 12” | Red with white fleck | **Purple Rooms** 1H1, 1H3, 1H4, 1H5, **Blue Rooms**, 4N53, 4N55, 4N63-67, 4N68, 4N70, 4N71-71B, **Yellow Rooms** 4Z1A, 4Z2-23, 4Y1-23 | 015a | Chrysotile |
| 12” x 12” | White with brown fleck | **Purple Rooms** Room 1A1, 1A1B, 1A6 , 1J12 **Blue Rooms** 1R9-10, 2S13-41A, 3U11B, 3U14, 3U16-18C, 3U24-27, 3V25-36, 3V38-42 and Corridor at Room 3V40, Rooms 4U17-20, 4N29-42, 3N43-44B, 4N46, 4N48-52, 4N55, Corridor adjacent to Room 4N44, **Red Rooms** shaft 43 first floor, 1F13-15, 2G4B, 2G23-25, 2G34-40, 3F7-32, 3FW1-W2, **Yellow Rooms** 2L5, 2S43-46A, 2SW25, 2SW4, 2S71-72, 2S7-7A, 2S9, 2S70, 2s48-53, 2R26-26A, 2R25A, 3V6- 23, 3V44-51, 3E25-27F, 3X30D, Corridors 3VC1 and adjacent to Room 3V51, 4NC14, 4VC1, 4V22E, 4V21, 4V1-18 | 017a | Chrysotile |
| 12” x 12” | Black | **Purple Room** 1A1B | 019a | Chrysotile |
| 12” x 12” | Beige with brown line | **Red Rooms** MM Red-server/phone room, 1D37, 1DC5 **Purple Rooms** 1A2, 1J6-10, 1P2, 1P3, 1P5, 1P10-13, 1P23B, 1P24, 1P25, 1N1-8 **Blue Rooms** 1U20-29, 1V2 & 10, 1P16-19, 1P26-27, 1PW2-3,1P6-8, 3N1A, 3N45, 3N49A, 3N29-42, Corridor 3NC1, Corridor adjacent to 3N52 and 3N26, Rooms 3UW1, 3U21-23 | 020a | Chrysotile |
| 12” x 12” | Grey with white line | **Purple Rooms** 1J2, 1J5-9, Purple Corridor 2AC1 **Yellow Rooms** corridor ITC1, 1RC3 (and blue) **Blue Rooms** 1R17 | 022a | Chrysotile |
| 12” x 12” | Light gray | **Red Rooms** Eng. Room 1D19, 1CC2 **Yellow Rooms** 1T1-6 (and sub rooms) | 023a | Chrysotile |
| 12” x 12” | Red with black fleck | **Yellow Rooms** 3Y1-21 and adjacent Corridors, **Blue Rooms** 1R1-5, 1RC3, 4NC3, **Purple Rooms** 2J24, 2J14, and Corridor adjacent to 2J14, Corridors 4NC3, 4HC6-9, Rooms 4H6-7, 4H9-10A, 4H29-29A, 4H39-41C | 025a | Chrysotile |
| 12” x 12” | Yellow | **Blue Room** 1V4-9 & 12-18 | 026a | Chrysotile |
| 12” x 12” | Dark gray with black fleck | **Blue Rooms** Nuclear Medicine Room 1PC1, 1P1B, 2P3-7B, 2P7C, 2N49A, 2N38, 2T13-16, 2T11, 2T10, 2U2-7, 2JW3 and Corridor 2UC1 | 027a | Chrysotile |
| 12” x 12” | Dark brown with brown fleck | Room 2EW4 and all Stairwells, **Blue Rooms** 3U5-9, 3N14-20, **Blue Corridor** 4NC6, **Red Rooms** 3B33A, 4D4, **Yellow Rooms** 3X26, 3U1-4 | 028a | Chrysotile |
| 12” x 12” | Brown with white fleck | Hallway adjacent to Red Room 2E16 | 030a | Chrysotile |
| 12” x 12” | Gray/green with brown fleck | Room 2J33, **Blue Rooms**, 4U7-16, Purple Rooms 2J26-33, 2J16-25 and adjacent Corridor, **Purple Rooms** 3H6, 3H8C-G, 3H21, 3H24, Corridor 3HC2 and Corridor adjacent to 3H7, 4H13-21, 4H24- 25B, 4H31-37, 4H1-5, 4HW1-2, 4H42-45, **Red Corridor** 3FC8, Red Rooms 4C1-22, 4GB1,4F11-21B, 4B26, 4C1-4C22, **Yellow Rooms** 2Pw3, 3W10C-10F, 3WC3, 3W11-15, 4U1-64V23-32, Corridors 4VC4, 4VC5 | 033a | Chrysotile |
| 12” x 12” | Beige with white/brown line | Corridor at Room 2CC3, **Blue Rooms** 2N32, 2N22A, 2N22B, 2N22C, 2N22, 22D, 22E, 22F, 2NW1,2NW2, 36A, 2N36, 2N13A, 2N14, 2N19, 2V11-16, 2VW1-2, 2NW5 2V3-8, 2V1 A-B, 2N4A, 2N49, 2N38, 2T8-9, Corridors 2NC3, 2NC6, Rooms 3N5, 3N5D-J, 3U29-30, 3N49, 3N49B-D, 3N3, 3N2, 3N11, 3N11B, 3N25A-G, 3N26A-J, 3N27A-H, 3N28A-H, 3N52A-G, 4N3-6, 4N8- 25, Corridor 4NC12A, **Purple Rooms** 2C12-13 and Corridor 2CC3, Purple Rooms 3H31, 3H35-35A, 3H39, 3H42-43A, 3H44-45, 3H51-57, 3H58-58B, Corridor adjacent to 4G40, **Red Rooms** 3V43A-43E, 3E9B, 4E9, 4E11-14, 4E18-19, 4G36D, **Yellow Rooms** 3E21A, 3E17A, 4G42-44, Corridor 4GC5, Rooms 4E6-4E11 | 034a | Chrysotile |
| 12” x 12” | Yellow with white fleck | **Blue Room** 2N33, 2N31, 2N30, 2N29, 2N27, 22N26, 2N24, 2N23, 4N77-83, Corridors 4Nc7, 4NC9, Corridors adjacent to Rooms 4N19, 4N37A and 4N36, **Purple Corridors** 3HC9, 3HC7, 3HC5, 3HC11, **Yellow Rooms** 2Q1-5, 2QJ2, 2Q7-13, 2QW7, 2Q24-28B, 3Z1-21A | 036a | Chrysotile |
| 12” x 12” | Orange | **Yellow Room** 2Q30, Corridor at **Blue Room** 3U31, | 041a | Chrysotile |
| 12” x 12” | Pink | Yellow Room 2S71A | 043a | Chrysotile |
| 12” x 12” | White | Corridor adjacent to Blue Room 4N22 | 054a | Chrysotile |
| 12” x 12” | Red | Corridor adjacent to Blue Room 4N22 | 055a | Chrysotile |
| 12” x 12” | Gray | Centre Stair to Purple | 010a-c | None |
| 12” x 12” | Beige with brown fleck | Corridor adjacent to Room 2G52, **Blue Room** 4N73, 4N75-75A, 4N84A-86, **Purple Rooms** 2BW3, 2BW4, 2B16-19, Corridor adjacent to **Red Room** 2G52, **Red Room** 3D1, 4D8, **Yellow Rooms** 4Y25-31, 4Z24-31, 4Z32B | 031a-c | None |

Vinyl floor tiles are non-friable and in good condition. ACM vinyl floor tiles may also be present in rooms not accessed during the original assessment. Remaining vinyl floor tiles within the building were not sampled due to the age of installation

**APPENDIX V - Vinyl Sheet Flooring – Paper Backing is Friable**

Seven visually distinct types of vinyl sheet flooring are present in the building, as follows:

| Pattern and Colour | Locations | Sample Numbers | Asbestos |
| --- | --- | --- | --- |
| Beige square pattern | **Purple Rooms** 1H2, Room 1A18, **Red Rooms** 2GW11-12, | 016a | Chrysotile |
| White/ grey/ green square | Room 2T7, **Blue Rooms** 2TW4, 2TC2, 2T1-2T7B, **Red Room** 4C31A, **Yellow Rooms** 2P1-2A, 2Q30ACorridor 2PC1, | 037a | Chrysotile |
| Brown with white square | Room 2SC9, **Blue Room** 3U10, 4N7, 4N28-28A, 4N74-76, **Red Rooms** 4G1-5, **Yellow Rooms** 2P2B-2E, 2P10-11, Corridor 2PC1, 2SC9, Rooms 2S4A, 2S5E, 2S8, 2S54-55A and adjacent Corridor, Rooms 2S68-69, 3X1-11E, 3X14-17 | 038a | Chrysotile |
| Dark green square | **Yellow** Emergency Area adjacent to Room 2R26B, **Yellow Rooms** 2R4A-4E | 042a | Chrysotile |
| Dark green/white square | Medical Corridors adjacent to Yellow Room 3X16, Rooms 3X18, 3X23-24, 3X31, 3X11A, 3X12 | 044a | Chrysotile |
| Red with green square | **Red Room** 4B30-31, **Yellow Rooms** 4Z32, 4Z33, | 047a | Chrysotile |
| Multi subdued colour pebble pattern | **Red Room** 1D6, 1D5 sheet vinyl currently covered with carpet | n/a | Chrysotile |
| Gray square | Surgical **Yellow Room** 4Z1, Corridor 4XC1 | 048a-c | None |

Asbestos present in vinyl sheet flooring is present in the paper backing (underpad) only. Vinyl sheet flooring is a non-friable material and is in good condition. All remaining types of vinyl sheet flooring throughout the building are non-asbestos due to the nature of the material (rubber and no underpad).

**Appendix MUMC – Asbestos Abated Area Survey**

**Level 1**

* 1K10D, 1K10E & Cafeteria flooring replacement Asbestos free materials. Interior partition walls ACM free. Ceiling tiles, flooring and interior partitions walls ACM free. All exterior perimeter walls to department contain ACM
* 1D1 Engineering carpet replaced with Asbestos free floor tiles. (1D1 – 1D13)
* 1R17/18, acoustic ceiling tiles, drywall, drywall compound and flooring replacement Asbestos free materials Flooring and ceiling tiles only, 1R6, 1R6A, 1R6B, 1R6C, 1R1, 1R2, 1R3, 1R4, 1R5, 1R7, 1R8, 1R.C1. All exterior perimeter walls to department contain ACM.
* Ewart Angus Center – level 1 and level 2 flooring replacement with asbestos free materials
* Williams Coffee Shop 1A2/2B1A, acoustic ceiling tiles, drywall, and drywall compound and flooring replacement Asbestos free materials.
* 1C area PAC ceiling tiles, flooring and new interior drywall all replaced. All exterior perimeter walls to department contain ACM
* 1C7 - asbestos free flooring, and ceiling tiles
* 1F renovation – Flooring is new
* 1D1 Volunteer Resources reception area and Volunteer lounge 1D4 carpet replaced with Asbestos free floor tiles.
* 1P42, 1P46 and 1P43 flooring replacement
* Partial texture coat removal from the King Street exit and near the yellow elevators of the parking garage

**Level 2**

* Main ring corridor Level 2
* 2Q Clinic – partial floor replacement (2Q1A and internal Clinic corridors only)
* 2H sheet flooring and ceiling tile asbestos free and interior walls. All exterior perimeter walls to department contain ACM
* School of Nursing main interior corridors sheet flooring and tile asbestos free
* 2L9, 2L9A, 2L9B drywall removed. All exterior perimeter walls to department contain ACM
* 2L2D, 2L2E, 2L2, 2L2B, 2L2A flooring replaced.
* 2L8B, 2L8A flooring replacement. Interior walls ACM removed. All exterior perimeter walls to department contain ACM
* 2S Registration to 2S10 staff station sheet flooring, ceiling tile and drywall asbestos free. All exterior perimeter walls to department contain ACM (this phase)
* 2S52 Endo Procedure Room new drywall ceiling and flooring installed. Interior walls new All exterior perimeter walls to department contain ACM
* 2S69 new interior walls and flooring new All exterior perimeter walls to department contain ACM
* 2Q53, 2QW3, 2Q52 and 2SC12 new flooring
* 2R6 new flooring and ceiling
* 2R11 new flooring and ceiling. Interior walls new. All exterior perimeter walls to department contain ACM
* 2RS1 new flooring.
* Open concept Stairwells red and yellow quadrants level 2 to 3 asbestos free tiles.
* 2F Phases 1 and 2 – Ceilings, and flooring are new. All interior partitions new. All exterior perimeter walls to department contain ACM. including 2G3 and 2G54A hallways.
* 2G Clinical areas, acoustic ceiling tiles, drywall, drywall compound and flooring replacement Asbestos free materials. All exterior perimeter walls to department contain ACM
* 2E24 Administration floor tiles replaced with wood veneer
* 2J24 acoustic ceiling tiles, drywall, drywall compound and flooring replacement Asbestos free materials. All exterior perimeter walls to department contain ACM
* 2JC1 flooring only. Entire 2C suite, new flooring and ceiling tiles, Also 2D suite, new floor and ceiling tiles, 2CW1 and 2CW2 .
* Chapel/worship centre – Flooring and ceilings are new
* Ceiling tiles Level 2 Red elevators to Yellow elevators straight through main lobby.
* 2C20, 2C19, 2C18, 2C17, 2C8A, 2C9A, 2C7 new flooring and ceiling tiles.
* 2S57 to 2S72 new flooring and ceiling tiles and internal/interior walls.
* 2S1, 2S1A, 2S1B, 2S1C, 2S1D, 2R18, 2S48, 2S49, 2S50, 2S51, 2S51A, 2S51B 2S52, 2S53A and 2S53B all ceiling tile, partitions and flooring removed and replaced.
* 2Q58, 2Q59, 2Q61, 2Q62, 2Q63, 2RC7, 2R3, 2R3A, 2R3B, 2R4, 2R4A, 2R4B, 2R4C, 2R4D, 2R4E, 2RC1, 2R20, 2R22, 2R21, RW8, R24, 2RJ2, 2R25, 2R25A, 2RW3 all ceiling tiles, partitions and flooring removed. Exterior walls still have original drywall.
* 2S2, 2SW1 and 2SC12A all ceiling tile, partitions and flooring removed. Some drywall removal (see figure).
* 2L7 ACM flooring and walls removed (see figure)
* 2Q42-2Q63 and 2RC1-2R20 drywall, flooring and ceiling ceiling tile removal (see figure)
* 2V3 Ceiling tile, floor tile and drywall removal (see figure)
* Old CT rooms (2S and 2Q) ceiling tiles, flooring and drywall removal (see figure):
* 2SC8 – ceiling tile, floor tile and partition walls removed (see figure May 27, 2013);
* 2SW6, 2S46A – ceiling tile, floor tile and partition walls removed (see figure May 27, 2013)
* 2PC1 - Ceiling tile removal from pre-op (u shape around nurces station)
* 2S11, 2S12, 2S13, 2S14, 2S15, 2SC1, 2S16, 2S19, 2S20, 2S21, 2S22, 2S23, 2S24, 2S25, 2S26, 2S27, 2S28, 2S29, 2S30, 2S31, 2S32, 2S33, 2S33, 2S34, 2S34, 2S35, 2S36, 2S37, 2S38, 2S39, 2S40, 2S41, 2S 59A, 2TW3, 2TW4, 2T8, 2T9, 2T10, 2T11, 2U5, 2U6, 2U7, 2U8, 2UC1 all ceiling tiles, partitions and flooring removed. Exterior walls still have original drywall

**Level 3**

* Main Ring Corridor Level 3 & Farncomb rear corridor (3H51 area) asbestos free sheet flooring
* 3V3 Clinic flooring tile and ceiling tile asbestos free. All exterior perimeter walls to department contain ACM
* 3H sheet flooring and ceiling tile asbestos free.
* 3F Clinic sheet flooring asbestos free. (3F23B, 3F23A, 3F23C, 3FC5, 3FC4, 3F29A, 3F30)
* 3F Clinic ceiling tiles asbestos free.
* 3B sheet flooring and ceiling tile asbestos free. All interior partitions walls asbestos free.
* All exterior perimeter walls to department contain ACM
* 3D sheet flooring and ceiling tile asbestos free. All interior partitions walls asbestos free excluding 3D21, 3D14, 3D15, 3D17, 3D16, 3D6, 3D11. All exterior perimeter walls to department contain ACM
* 3C sheet flooring asbestos free
* Ronald McDonald Family Room flooring, ceiling tiles and inner walls asbestos free – NOTE outer perimeter walls are still original and are to be considered as to contain asbestos joining compound.
* 3V ENT Clinic– Ceiling tiles, flooring and most walls are new. All exterior perimeter walls to department contain ACM
* 3A GFT area– Ceilings, and floors are new. All interior partitions walls ACM free. All exterior perimeter walls to department contain ACM
* 3D – Sedation clinic – sheet flooring and ceiling tile, drywall and drywall compound ACM free. All exterior perimeter walls to department contain ACM
* 3N5/Courtyoard 3, acoustic ceiling tiles, drywall, drywall compound and flooring replacement Asbestos free materials includes 3N5A, 3N5B, 3NW1, 3NW2, 3N51 suite, new flooring and ceiling tiles. All exterior perimeter walls to department contain ACM
* Floor tile replacement with sheet flooring: corridor 3H31,
* 3G Inpatient Ward, acoustic ceiling tiles, drywall, drywall compound and flooring replacement Asbestos free materials. All exterior perimeter walls to department contain ACM
* main corridor ward  3Y ceiling tiles replaced with new.
* Ceiling tiles removed from 3WC1 and replaced with new.
* Ceiling Tiles, Drywall and Floor tile removed from 3V (3V26A, 3V26, 3V25, 3V23B, 3V23A, 3V23C, 3V20, 3V21, 3V22, 3V24, 3VC8, 3VC4, 3V19A, 3V19, 3V18, 3V17, 3V16B, 3V16A, 3V16, 3V16C, 3V15, 3V14, 3V13, 3V13A)

**Level 4**

* Floor tile replacement with sheet flooring: corridors 4HC1, 4NC2 and 4NC1.
* Main Ring Corridor Level 4 asbestos free sheet flooring **except:** 4N48 to 4N43 original carpeting
* 4H24 new flooring and ceiling tiles
* 4N72 acoustic ceiling tiles, drywall, drywall compound and flooring replacement
* 4A ceiling tiles, flooring and interior partitions walls ACM free. All exterior walls to department contain ACM.
* 4X ceiling tiles, flooring and interior partitions walls ACM free. All exterior walls to department contain ACM.
* 4H32 / 4H34 new vinyl floor tiles
* 4G1 to 4G5 new flooring and ceiling tiles and internal/interior walls.
* 4F1 to 4F9B new flooring and ceiling tiles and internal/interior walls.
* 4H41 floor tiles and ceiling tiles replaced. Firestoping also removed from the lab sinks.
* 4Z – complete floor tile, drywall and ceiling tile removal. Exterior drywall remains
* 4W - complete floor tile, drywall and ceiling tile removal. Exterior drywall remains