Summary of Asbestos Locations Hamilton Health Sciences, West Lincoln Memorial Hospital – March 2020

**Main Hospital - Front Wing (1948)**

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | **Basement Level** |  |  |  |
| **Material** | **Locations** | **Approx. Quantity** | **Sample Number(s)** | **Result (if ACM)** |
| Parging Cement | Throughout Building on Pipe Fittings:  Locker Room, Inventory Storage, Inventory Room, Loading Area, Central Service Rooms, Surgery Tool Disinfecting Room, Offices #1 to #9, Board Room, Admin/Medical Affairs Office, Staff Washroom, PM. Office, Records Retention, Maintenance Shop, Boiler Room, Laundry Room, Linen Storage, Linen Sorting, Storage Rooms, Corridor, and Stairwells. | 1500 Fittings | N/A | Chrysotile |
| Aircell | Throughout Building on Straight Sections of Pipe:  Locker Room, Inventory Storage, Inventory Room, Loading Area, Central Service Rooms, Surgery Tool Disinfecting Room, Offices #1 to #9, Board Room, Admin/Medical Affairs Office, Staff Washroom, PM. Office, Records Retention, Maintenance Shop, Boiler Room, Laundry Room, Linen Storage, Linen Sorting, Storage Rooms, Corridor, and Stairwells. | 2000 LF | N/A | Chrysotile |
| VFT – 12”x12” Dark Green with White Streaks | Basement Office #1 | 400 SF | 0006A | VFT - Chrysotile  Mastic – None Detected |
| VFT – 12”x12” Yellow with White Streaks | Basement Office #1 | <1 SF | 0007A and 0006A-C Phase b | VFT - Chrysotile  Mastic – None Detected |
| VFT – 9”x9” Green with White Streaks | Basement Locker Room, Inventory Storage, and Washroom in Office #6 | 900 SF | 0013A | VFT - Chrysotile  Mastic – None Detected |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | **Ground Floor** |  |  |  |
| **Material** | **Locations** | **Approx. Quantity** | **Sample Number(s)** | **Result (if ACM)** |
| Parging Cement | Throughout Building on Pipe Fittings:  Stairwells. | N/A | N/A | Chrysotile |
| Aircell | Throughout Building on Straight Sections of Pipe:  Stairwells. | N/A | N/A | Chrysotile |
| VFT – 12”x12” Dark Green with White Streaks | Ground Floor Wash Area | 100 SF | 0006A | VFT - Chrysotile  Mastic – None Detected |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | **First Floor** |  |  |  |
| **Material** | **Locations** | **Approx. Quantity** | **Sample Number(s)** | **Result (if ACM)** |
| Parging Cement | Throughout Building on Pipe Fittings:  Corridor (Beneath Floor Hatches). | N/A | N/A | Chrysotile |
| Aircell | Throughout Building on Straight Sections of Pipe:  Corridor (Beneath Floor Hatches). | N/A | N/A | Chrysotile |
| VSF - Orange Fleck | First Floor Staff Lounge and Washroom | 400 SF | 0043A | Chrysotile |
| VSF - Grey and White Squares | First Floor Medical Storage | 100 SF | 0046A | Chrysotile |
| VFT – 12”x12” Grey with Brown and White Streaks with White Streaks | First Floor Storage Closets | 200 SF | 0044A-C | VFT - Chrysotile  Mastic – None Detected |
| Paper Heat Shields | First Floor Storage Closets | 2 Heat Shields | 0045A | Chrysotile |

**Main Hospital - Middle Wing (1960's)**

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | **Basement Level** |  |  |  |
| **Material** | **Locations** | **Approx. Quantity** | **Sample Number(s)** | **Result (if ACM)** |
| Parging Cement | Throughout Building on Pipe Fittings:  Mechanical Room, Physio Department, Offices, Accounting Department, Conference Area, Washrooms, Waiting Room, File Storage, Mechanical Room, Medical File Storage, Electrical Room, Corridors, Vestibules, and Stairwells. | 1500 Fittings | N/A | Chrysotile |
| Parging Cement on Cushion Tank | Basement Mechanical Room | 30 SF | N/A | Chrysotile |
| VFT – 9”x9” Beige with Grey Streaks | File Storage Room, East Corridor, Waiting Room, Vestibule, Accounting Department, Main Corridor and Stairwells. | N/A | 019A | VFT - Chrysotile  Mastic – Chrysotile |
| VFT – 12”x12” Dark Green with White Streaks | Basement Main Corridor | 200 SF | 0006A | VFT - Chrysotile  Mastic – None Detected |
| Transite Board (Above Ceiling) | Basement Medical Storage Room  South End of the Main Corridor | 400 SF  100 SF | N/A | Presumed ACM |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | **Ground Floor** |  |  |  |
| **Material** | **Locations** | **Approx. Quantity** | **Sample Number(s)** | **Result (if ACM)** |
| Parging Cement | Throughout Building on Pipe Fittings:  Washrooms, Cleaning Room, Dressing Room #1, Dark Room, Nurses Station, Waiting Room, Corridor. | N/A | N/A | Chrysotile |
| VSF - Brown with White Squares | Ground Floor Barrier-Free Shower | 100 SF | 0040A | Chrysotile |
| VFT – 9”x9” Beige with Grey Streaks | Main Corridor, Dressing Room #1 and #2, Radiology Suite, Patient Rooms, Linen Storage, Nurses Station, Office and Stairwells. | N/A | 019A | VFT - Chrysotile  Mastic – Chrysotile |
| VFT – 12”x12” Dark Green with White Streaks | Ground Floor Main Corridor | 200 SF | 0006A | VFT - Chrysotile  Mastic – None Detected |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | **First Floor** |  |  |  |
| **Material** | **Locations** | **Approx. Quantity** | **Sample Number(s)** | **Result (if ACM)** |
| Parging Cement | Throughout Building on Pipe Fittings:  Operating Department, Janitors Closet, Washroom, Closets within Patient Rooms. | N/A | N/A | Chrysotile |
| VFT – 9”x9” Beige with Grey Streaks | Main Corridor, Patient Rooms, Offices, Accessible Areas in Operating Department, Intensive Care Unit, Waiting Room and Stairwells. | N/A | 019A | VFT - Chrysotile  Mastic – Chrysotile |

**Main Hospital - ER Wing (1970's)**

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | **Basement Level** |  |  |  |
| **Material** | **Locations** | **Approx. Quantity** | **Sample Number(s)** | **Result (if ACM)** |
| Parging Cement | Basement Mechanical Room | 200 Fittings | N/A | Chrysotile |
| VFT – 12”x12” Yellow with White Streaks | Basement Corridors | N/A | 0007A | VFT - Chrysotile  Mastic – None Detected |
| VFT – 12”x12” Beige with Thin Brown Streaks | Labs, Offices, Lounge, ECG Department and File Storage. | 5000 SF | 00027A | VFT - Chrysotile  Mastic – None Detected |
| CT - 24"x48" Lay-in Pinhole and Texture Pattern | Basement ECG Department (Mixed with Non ACM Ceiling Tiles) | 50 SF | 0030A | Amosite |
| Transite Board | Basement Corridor Former Vestibule Entrance, North End of the Basement Main Corridor, Lounge and Lab #2 | 60 SF | N/A | Presumed ACM |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | **Ground Floor** |  |  |  |
| **Material** | **Locations** | **Approx. Quantity** | **Sample Number(s)** | **Result (if ACM)** |
| VFT – 12”x12” Yellow with White Streaks | Ground Floor ER Waiting Room | N/A | 0007A | VFT - Chrysotile  Mastic – None Detected |
| VFT – 12”x12” Beige with Thin Brown Streaks | Palliative Care Department, Break Room and Patient Rooms in the ER Department, EMS Room Closet. | 2000 SF | 00027A | VFT - Chrysotile  Mastic – None Detected |
| Transite Board | Exterior Entrance to ER Department | 500 SF | N/A | Presumed ACM |

**Main Hospital - Kitchen Area (1986)**

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | **Ground Floor** |  |  |  |
| **Material** | **Locations** | **Approx. Quantity** | **Sample Number(s)** | **Result (if ACM)** |
| Transite Pipe (Rain Water Leaders) | Service Corridor  Kitchen, Office, and Dish Room  Ingredients Storage Room  Dry Good Storage  Cafeteria  Ladies' Locker Room and Washroom Area  Halfway Café Lounge  Men's Locker Room and Washroom Area | 6 LF  100 LF  20 LF  20 LF  40 LF  25 LF  15 LF  30 LF | N/A | Presumed ACM |

**Alexander Globe Centre - Former Nurses' Residence (1948)**

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | **Attic Level** |  |  |  |
| **Material** | **Locations** | **Approx. Quantity** | **Sample Number(s)** | **Result (if ACM)** |
| Aircell | Attic (Visible above Hatches within Washroom and Mechanical Room) | 80 LF | N/A | Chrysotile |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | **Ground Floor** |  |  |  |
| **Material** | **Locations** | **Approx. Quantity** | **Sample Number(s)** | **Result (if ACM)** |
| VFT – 9”x9” Beige with Red Streaks | Janitor’s Closet, Stationery Closet, and Sprinkler Room | 80 SF | 0060A-C | VFT - Chrysotile  Mastic – Chrysotile |
| VFT – 12”x12” Beige with Orange Flecks | Vestibule, Washroom in PC Room #1, and Front Entrance | 350 SF | 0061A-C | VFT – None Detected  Mastic – Chrysotile |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | Exterior |  |  |  |
| Material | Locations | Approx. Quantity | Sample Number(s) | Result (if ACM) |
| Transite Panels | Exterior Siding | 5000 SF | N/A | Presumed ACM |